## QUOTATION NOTICE
VIDYA INTERNATIONAL CHARITABLE TRUST VAST Campus, Thalakkottukara, Thrissur - 680 501 Tel: 04885 287751 / 52 Email: vidyaict@vidyaacademy.ac.in
VAST Campus, Thalakkottukara PO, Thrissur - 680 501 Tele: 04885 287751/52 Fax: 04885 288366
Ref No:VAST /FIRE FIGHTING-DECENNIAL BLOCK/2017-18 | [5 empty] | 2018-03-26
NAME OF WORK: Supplying, Installing, Testing and Commissioning of Fire Fighting system at Decennial block, VAST,Thalakkottukara
TENDER SHEDULE
Sealed Competetive Tenders in the prescribed format are invited from experienced and established suppliers/contractors for the works described below. All terms and Conditions pertaining to the tender should invariably be furnished at the first instance itself. Documents if any to prove authentic representation of the product/work quoted and previous experience in the field may be attached along with the tender.
Sl.No | Item | Make | Specification | Qty. | Rate | Amount
1 | Terrace Pump:- Supply, Installation, Testing and Commissioning (SITC) of fire fighting Motor-pump set,900 LPS, 36 M Head horizondal, end section, centrifugal electronic driven auto start standby pump coforming to IS 1520 | KIRLOSKAR/ CROMPTON | Motor:5 HP, 3 phase,415 volts, 50Hz, 2900 RPM. Pump:Delivery: 900 Litre per Hour Horizondal head: 36 m | 1 No
2 | Air Release Valve:- SITC of air release valve as per IS 778 | ATOM or KARTAR | 20 mm dia, Gun Metal | 1 No
3 | Above Ground Piping:- SITC MS ERW black B class pipe with fitting as per IS 1239. Pipe shall be coated with oil primer and two coats of post office red colour paint of IS 536 | TATA/JINDAL | 100 mm dia, Class B MS pipe IS 1239 | 145 M
3a | …………………………Do………………………………………………………….. | TATA/JINDAL | 80 mm Dia | RO
4 | Butterfly Valve:- SITC of multipurpose soft seated water butterfly valve having centric disc construction, single piece body replaceable or bondable rubber seat to give 100% tight shut on both flow direction against vaccum | KARTHAR ISI/ CASTLE/ INTERVALVE | 100 mm, PN 16, CI/SS IS 13095 | 2 Nos.
5 | Non-Return Valve:- SITC of cast iron non-return valve as per IS 5312 | KARTHAR/ CASTLE/ INTERVALVE | 100 mm dia, CI/SS, Horizondal IS 5312 | 1 No
6 | Hose Reel:- SITC of hydraulic hose reel complete with swing type drum,MS construction spray painted in post office red drum and brackets conforming to IS 884 with 19 mm dia rigid hose having length of 25 m with stop coke and nozzle on one end and all other necessary fittings. | SECULITE/ READE/ NEWAGE/ FIRESTONE | 19/20 mm, Thermoplastic, Textile reinforced IS 12585 | 9 Nos.
7 | Ball Valve:- SITC of Ball valve arrangement for fire duct.IS 5312 | KARTHAR/ PRIME | SS/GM, 25 MM | 9 Nos.
8 | Fire Brigade Inlet:- SITC of2 way fire brigade inlet connection fabricated from 100 mm dia MS Class B medium grade pipe comprising of three 63 mm gun metal made threaded non return valve | KARTHAR/ NEWAGE /ARIHANT | 63 MM, Brass/GM 2way | 1 No.
9 | Sign Board;- Supply and Installation of photo luminous type direction and exit sign boards as follows: -
9a | ASSEMBLY AREA |  | 1 ft X 4 ft | 1 No
9b | FIRE EXIT,EXIT,FIRE DUCT and NO SMOKING |  | 3 mm thick PVC foam board size 12'x 4" | 4X9
10 | Fire Extinguisher:- Supply and errection of DCP type fire extinguisher. | SHEYAS/ SAFEX/ OMAX/ FIRE STONE | IS:15683, ABC type -4 kg Capacity Mono Ammonium Phosphate Powder , Stored Pressure Type,Pressure Gauge, Controllable discharge mechanism, as per IS 15683 ISI mark. | 9 Nos.
11 | Scutiny, Incidental, inspection and any other statutory fee including granting of FIRE NOC.
Terms & Conditions
A | Last Date of Receipt | 2018-04-05
B | EMD | Nil
C | Validity | 30 days
D | Price | Inclusive of GST & all other taxes
E | Delivary Period / Period of Completion | 2 Weeks
F | Warranty/ Guarantee | 3 Years
I | Payment Terms | After completion and commission of work
J | Agreement | Agreement to be executed in stamp paper worth Rs.200/-
K | Security Deposit | 5% of contract value by DD/Remittance at the bank A/c
L | Invoice | To be prepared in favour of The Executive Director, VICT, Thrissur
M | Bank Charges | At contractor's Account
(Sd)
EXECUTIVE DIRECTOR